## Sheet1
H Panel Modbus Register Mapping
Channel Name | Channel # | Register(s) (Decimal) | Bit | Mask | # of Words
Typical H panel Gas fueled unit
- <Analog_Input_Channels>
OIL TEMP | 1 | 140 | N/A | N/A | 1 | Unsigned Integer
COOLANT TEMP | 2 | 142 | N/A | N/A | 1
OIL PRESSURE | 3 | 144 | N/A | N/A | 1
COOLANT LEVEL | 4 | 146 | N/A | N/A | 1
USER CFG 05/Fuel Level | 5 | 148 | N/A | N/A | 1
USER CFG 06 | 6 | 150 | N/A | N/A | 1
THROT POS | 7 | 152 | N/A | N/A | 1
O2 SENSOR | 8 | 154 | N/A | N/A | 1
BAT CHARGE CUR | 9 | 156 | N/A | N/A | 1
BATTERY VOLTS | 10 | 158 | N/A | N/A | 1
CURRENT PHS A | 11 | 160 | N/A | N/A | 1
CURRENT PHS B | 12 | 162 | N/A | N/A | 1
CURRENT PHS C | 13 | 164 | N/A | N/A | 1
AVRG CURRENT | 14 | 166 | N/A | N/A | 1
VOLT PHS A-B | 15 | 168 | N/A | N/A | 1
VOLT PHS B-C | 16 | 170 | N/A | N/A | 1
VOLT PHS C-A | 17 | 172 | N/A | N/A | 1
AVRG VOLTAGE | 18 | 174 | N/A | N/A | 1
TOTAL POWER KW | 19 | 176 | N/A | N/A | 1
TOTAL PF | 20 | 178 | N/A | N/A | 1
GEN FREQUENCY | 21 | 180 | N/A | N/A | 1
ENGINE RPM | 22 | 182 | N/A | N/A | 1
A/F DUTY CYCLE | 23 | 184 | N/A | N/A | 1
- <Digital_Input_Channels>
AUTO SWITCH | 1 | 129 | 15 | 0x8000 | N/A
MANUAL SWITCH | 2 | 129 | 14 | 0x4000 | N/A
EMERGENCY STOP | 3 | 129 | 13 | 0x2000 | N/A
REMOTE START | 4 | 129 | 12 | 0x1000 | N/A
BAT CHRGR FAIL | 5 | 129 | 11 | 0x0800 | N/A
DI2/FUEL PRESSURE | 6 | 129 | 10 | 0x0400 | N/A
DI3/LINE POWER | 7 | 129 | 9 | 0x0200 | N/A
DI4/GEN POWER | 8 | 129 | 8 | 0x0100 | N/A
MODEM DCD | 9 | 129 | 7 | 0x0080 | N/A
MODEM ENABLED | 10 | 129 | 6 | 0x0040 | N/A
GEN OVERSPEED | 11 | 129 | 5 | 0x0020 | N/A
HUIO 1 CFG 12 | 12 | 129 | 4 | 0x0010 | N/A
HUIO 1 CFG 13 | 13 | 129 | 3 | 0x0008 | N/A
HUIO 1 CFG 14 | 14 | 129 | 2 | 0x0004 | N/A
HUIO 1 CFG 15 | 15 | 129 | 1 | 0x0002 | N/A
HUIO 2 CFG 16 | 16 | 129 | 0 | 0x0001 | N/A
HUIO 2 CFG 17 | 17 | 130 | 15 | 0x8000 | N/A
HUIO 2 CFG 18 | 18 | 130 | 14 | 0x4000 | N/A
HUIO 2 CFG 19 | 19 | 130 | 13 | 0x2000 | N/A
HUIO 3 CFG 20 | 20 | 130 | 12 | 0x1000 | N/A
HUIO 3 CFG 21 | 21 | 130 | 11 | 0x0800 | N/A
HUIO 3 CFG 22 | 22 | 130 | 10 | 0x0400 | N/A
HUIO 3 CFG 23 | 23 | 130 | 9 | 0x0200 | N/A
HUIO 4 CFG 24 | 24 | 130 | 8 | 0x0100 | N/A
HUIO 4 CFG 25 | 25 | 130 | 7 | 0x0080 | N/A
HUIO 4 CFG 26 | 26 | 130 | 6 | 0x0040 | N/A
HUIO 4 CFG 27 | 27 | 130 | 5 | 0x0020 | N/A
- <Digital_Output_Functions> |  | 1 |  |  | N/A
COMMON ALARM | 1 | 131 | 15 | 0x8000 | N/A
COMMON WARNING | 2 | 131 | 14 | 0x4000 | N/A
GEN RUNNING | 3 | 131 | 13 | 0x2000 | N/A
ALARMS ENABLED | 4 | 131 | 12 | 0x1000 | N/A
READY FOR LOAD | 5 | 131 | 11 | 0x0800 | N/A
GEN READY TO RUN | 6 | 131 | 10 | 0x0400 | N/A
GEN STOPPED-ALRM | 7 | 131 | 9 | 0x0200 | N/A
GEN STOPPED | 8 | 131 | 8 | 0x0100 | N/A
GEN IN MANUAL | 9 | 131 | 7 | 0x0080 | N/A
GEN IN AUTO | 10 | 131 | 6 | 0x0040 | N/A
GEN IN OFF | 11 | 131 | 5 | 0x0020 | N/A
OVERCRANK ALARM | 12 | 131 | 4 | 0x0010 | N/A
OIL INHIBIT ALRM | 13 | 131 | 3 | 0x0008 | N/A
ANNUNC SPR LIGHT | 14 | 131 | 2 | 0x0004 | N/A
OIL TEMP HI ALRM | 15 | 131 | 1 | 0x0002 | N/A
OIL TEMP LO ALRM | 16 | 131 | 0 | 0x0001 | N/A
OIL TEMP HI WARN | 17 | 132 | 15 | 0x8000 | N/A
OIL TEMP LO WARN | 18 | 132 | 14 | 0x4000 | N/A
OIL TEMP FAULT | 19 | 132 | 13 | 0x2000 | N/A
COOL TMP HI ALRM | 20 | 132 | 12 | 0x1000 | N/A
COOL TMP LO ALRM | 21 | 132 | 11 | 0x0800 | N/A
COOL TMP HI WARN | 22 | 132 | 10 | 0x0400 | N/A
COOL TMP LO WARN | 23 | 132 | 9 | 0x0200 | N/A
COOL TMP FAULT | 24 | 132 | 8 | 0x0100 | N/A
OIL PRES HI ALRM | 25 | 132 | 7 | 0x0080 | N/A
OIL PRES LO ALRM | 26 | 132 | 6 | 0x0040 | N/A
OIL PRES HI WARN | 27 | 132 | 5 | 0x0020 | N/A
OIL PRES LO WARN | 28 | 132 | 4 | 0x0010 | N/A
OIL PRES FAULT | 29 | 132 | 3 | 0x0008 | N/A
COOL LVL HI ALRM | 30 | 132 | 2 | 0x0004 | N/A
COOL LVL LO ALRM | 31 | 132 | 1 | 0x0002 | N/A
COOL LVL HI WARN | 32 | 132 | 0 | 0x0001 | N/A
COOL LVL LO WARN | 33 | 133 | 15 | 0x8000 | N/A
COOL LVL FAULT | 34 | 133 | 14 | 0x4000 | N/A
ANALOG 5 HI ALRM | 35 | 133 | 13 | 0x2000 | N/A
ANALOG 5 LO ALRM | 36 | 133 | 12 | 0x1000 | N/A
ANALOG 5 HI WARN | 37 | 133 | 11 | 0x0800 | N/A
ANALOG 5 LO WARN | 38 | 133 | 10 | 0x0400 | N/A
ANALOG 5 FAULT | 39 | 133 | 9 | 0x0200 | N/A
ANALOG 6 HI ALRM | 40 | 133 | 8 | 0x0100 | N/A
ANALOG 6 LO ALRM | 41 | 133 | 7 | 0x0080 | N/A
ANALOG 6 HI WARN | 42 | 133 | 6 | 0x0040 | N/A
ANALOG 6 LO WARN | 43 | 133 | 5 | 0x0020 | N/A
ANALOG 6 FAULT | 44 | 133 | 4 | 0x0010 | N/A
GOV POS HI ALARM | 45 | 133 | 3 | 0x0008 | N/A
GOV POS LO ALARM | 46 | 133 | 2 | 0x0004 | N/A
GOV POS HI WARN | 47 | 133 | 1 | 0x0002 | N/A
GOV POS LO WARN | 48 | 133 | 0 | 0x0001 | N/A
GOV POS FAULT | 49 | 134 | 15 | 0x8000 | N/A
OXYGEN HI ALARM | 50 | 134 | 14 | 0x4000 | N/A
OXYGEN LO ALARM | 51 | 134 | 13 | 0x2000 | N/A
OXYGEN HI WARN | 52 | 134 | 12 | 0x1000 | N/A
OXYGEN LO WARN | 53 | 134 | 11 | 0x0800 | N/A
O2 SENSOR FAULT | 54 | 134 | 10 | 0x0400 | N/A
CHG CURR HI ALRM | 55 | 134 | 9 | 0x0200 | N/A
CHG CURR LO ALRM | 56 | 134 | 8 | 0x0100 | N/A
CHG CURR HI WARN | 57 | 134 | 7 | 0x0080 | N/A
CHG CURR LO WARN | 58 | 134 | 6 | 0x0040 | N/A
CHG CURR FAULT | 59 | 134 | 5 | 0x0020 | N/A
BAT VOLT HI ALRM | 60 | 134 | 4 | 0x0010 | N/A
BAT VOLT LO ALRM | 61 | 134 | 3 | 0x0008 | N/A
BAT VOLT HI WARN | 62 | 134 | 2 | 0x0004 | N/A
BAT VOLT LO WARN | 63 | 134 | 1 | 0x0002 | N/A
AVG CURR HI ALRM | 64 | 134 | 0 | 0x0001 | N/A
AVG CURR LO ALRM | 65 | 135 | 15 | 0x8000 | N/A
AVG CURR HI WARN | 66 | 135 | 14 | 0x4000 | N/A
AVG CURR LO WARN | 67 | 135 | 13 | 0x2000 | N/A
AVG VOLT HI ALRM | 68 | 135 | 12 | 0x1000 | N/A
AVG VOLT LO ALRM | 69 | 135 | 11 | 0x0800 | N/A
AVG VOLT HI WARN | 70 | 135 | 10 | 0x0400 | N/A
AVG VOLT LO WARN | 71 | 135 | 9 | 0x0200 | N/A
TOT PWR HI ALARM | 72 | 135 | 8 | 0x0100 | N/A
TOT PWR LO ALARM | 73 | 135 | 7 | 0x0080 | N/A
TOT PWR HI WARN | 74 | 135 | 6 | 0x0040 | N/A
TOT PWR LO WARN | 75 | 135 | 5 | 0x0020 | N/A
GEN FREQ HI ALRM | 76 | 135 | 4 | 0x0010 | N/A
GEN FREQ LO ALRM | 77 | 135 | 3 | 0x0008 | N/A
GEN FREQ HI WARN | 78 | 135 | 2 | 0x0004 | N/A
GEN FREQ LO WARN | 79 | 135 | 1 | 0x0002 | N/A
GEN FREQ FAULT | 80 | 135 | 0 | 0x0001 | N/A
ENG RPM HI ALARM | 81 | 136 | 15 | 0x8000 | N/A
ENG RPM LO ALARM | 82 | 136 | 14 | 0x4000 | N/A
ENG RPM HI WARN | 83 | 136 | 13 | 0x2000 | N/A
ENG RPM LO WARN | 84 | 136 | 12 | 0x1000 | N/A
ENG RPM FAULT | 85 | 136 | 11 | 0x0800 | N/A
SWITCH IN AUTO | 86 | 136 | 10 | 0x0400 | N/A
SWITCH IN MANUAL | 87 | 136 | 9 | 0x0200 | N/A
E-STOP ACTIVE | 88 | 136 | 8 | 0x0100 | N/A
REMOTE START ACT | 89 | 136 | 7 | 0x0080 | N/A
BATT CHARGE FAIL | 90 | 136 | 6 | 0x0040 | N/A
LOW FUEL PRS ACT | 91 | 136 | 5 | 0x0020 | N/A
DI3/LINE PWR ACT | 92 | 136 | 4 | 0x0010 | N/A
DI4/GEN PWR ACT | 93 | 136 | 3 | 0x0008 | N/A
LINE POWER | 94 | 136 | 2 | 0x0004 | N/A
GEN POWER | 95 | 136 | 1 | 0x0002 | N/A
ILC ALR/WRN #1 | 96 | 136 | 0 | 0x0001 | N/A
ILC ALR/WRN #2 | 97 | 137 | 15 | 0x8000 | N/A
IN WARM UP | 98 | 137 | 14 | 0x4000 | N/A
IN COOL DOWN | 99 | 137 | 13 | 0x2000 | N/A
CRANKING | 100 | 137 | 12 | 0x1000 | N/A
NEED SERVICE | 101 | 137 | 11 | 0x0800 | N/A
SHUTDOWN GENSET | 102 | 137 | 10 | 0x0400 | N/A
CHCK V PHS ROT | 103 | 137 | 9 | 0x0200 | N/A
CHCK C PHS ROT | 104 | 137 | 8 | 0x0100 | N/A
FAULT RLY ACTIVE | 105 | 137 | 7 | 0x0080 | N/A
USR CONFIG 106 | 106 | 137 | 6 | 0x0040 | N/A
INT EXERCISE ACT | 107 | 137 | 5 | 0x0020 | N/A
CHECK FOR ILC | 108 | 137 | 4 | 0x0010 | N/A
USR CONFIG 109 | 109 | 137 | 3 | 0x0008 | N/A
USR CONFIG 110 | 110 | 137 | 2 | 0x0004 | N/A
USR CONFIG 111 | 111 | 137 | 1 | 0x0002 | N/A
USR CONFIG 112 | 112 | 137 | 0 | 0x0001 | N/A
USR CONFIG 113 | 113 | 138 | 15 | 0x8000 | N/A
USR CONFIG 114 | 114 | 138 | 14 | 0x4000 | N/A
USR CONFIG 115 | 115 | 138 | 13 | 0x2000 | N/A
USR CONFIG 116 | 116 | 138 | 12 | 0x1000 | N/A
USR CONFIG 117 | 117 | 138 | 11 | 0x0800 | N/A
USR CONFIG 118 | 118 | 138 | 10 | 0x0400 | N/A
RPM MISSING | 119 | 138 | 9 | 0x0200 | N/A
RESET ALARMS | 120 | 138 | 8 | 0x0100 | N/A
ENGINE HOURS NOW | N/A | 304 | N/A | N/A | 2 | Unsigned Integer
Information on Modbus Register positions:
Register maps can start from 0 or 1. Our spreadsheet Modbus map that we send out to the market is set-up based on the first Register being 1 (more typical within the market).
Other internal documents from our development team is based on a starting register of 0.
1 word = 2 bytes = 16 bits = 1 register
All of our analog parameters can be addressed with a single 1 word register with the exception of run hours (note: kWhrs would be affected but not currently listed on map).
Technically, the analog architecture is setup for 2 word registers with the higher bits in the lower register. Example (140 is the lower bits for oil temp, 139 would be higher bits). This is why the registers increase by two.
The spreadsheet Modbus map that we send out, directly references the correct address for the lower bits when using a register map that starts with 1.
The run hours can exceed the lower bit register for applications exceeding 6,553.6 of run hours. This typicaly occurs in prime power applications.
Run hours address (starting from 1) is 306 for the lower bits and 305 for the upper bits. (Most applications will be fine just reading 1 word – register 306.)
Base 0: 0, 1, 2… 138, 139, (OIL TEMP) 140, 141 (COOLANT TEMP)…. 304, 305 (Run Hours)
Base 1: 1, 2, 3… 139, 140, (OIL TEMP) 141, 142 (COOLANT TEMP)…. 305, 306 (Run Hours) --- Please use base 1 information when communicating with customers.